## Winding Resistance and Loss
Aletheia template resistance v2
Fill in the yellow cells as on the paper logsheet. Grey cells are printed text or are calculated; they are locked. Choose from the list where a cell offers one; readings must be numbers and dates must be dates (dd-mm-yyyy). Leave a cell empty if the value is not on the sheet: it is recorded as NA.
SHORT CIRCUIT LABORATORY
LOG-SHEET FOR LOSS MEASUREMENT ON TRANSFORMER: Measurement of Resistance
Test Series No |  |  | 25T1656 |  |  | Before STC test : Date |  |  | 2025-10-29
Sample no |  |  | HVD25S0847 |  |  | After STC test : Date |  |  | 2025-11-04
Serial no. | [5 empty] | Rated kVA
Customer | [5 empty] | Winding Material: Copper / Aluminium
Manufacturer | [5 empty] | Rated voltage (HV / LV)
Measurement of Resistance |  |  |  | Before STC test |  |  |  | After STC test
Temperature top oil - °C |  |  |  | 25.5 |  |  |  | 27
Temperature bottom oil - °C |  |  |  | 23.9 |  |  |  | 24.8
Resistance of H.V. winding in Ohms / milli-Ohms / micro-Ohms
Tap Pos. | Voltage ratio | Before STC Test |  |  | After STC Test
|  | 1U1V | 1V1W | 1W1U | 1U1V | 1V1W | 1W1U
N |  | 3.9736 | 3.9558 | 3.969 | 3.989 | 3.9734 | 3.9864
H |  | 4.2028 | 4.1822 | 4.1874 | 4.22 | 4.1988 | 4.2092
L |  | 3.5476 | 3.5398 | 3.5458 | 3.5612 | 3.554 | 3.5622
Resistance of L.V. winding in Ohms / milli-Ohms / micro-Ohms
Before STC Test |  |  | After STC Test
2u2v | 2v2w | 2w2u | 2u2v | 2v2w | 2w2u
3.8716 | 3.865 | 3.9074 | 3.897 | 3.8844 | 3.9248
Customer's Signature | [5 empty] | Test Engineer
APPROVED BY: Document: FORMS & FORMATS SECTION : 56 PAGE NO. 1 OF 1 ISSUE NO. 01 REVISION NO.: 00 DATE : 01.06.2019