## Routine Test Logsheet
Aletheia template routine v2
Fill in the yellow cells as on the paper logsheet. Grey cells are printed text or are calculated; they are locked. Choose from the list where a cell offers one; readings must be numbers and dates must be dates (dd-mm-yyyy). Leave a cell empty if the value is not on the sheet: it is recorded as NA.
SHORT CIRCUIT LABORATORY
Log sheet for routine tests on Transformers
Test Series Number |  |  | 25T1654 |  |  | Sample Number |  | HVD25S0867
Customer / Manufacturer
Date |  |  |  | BT |  |  | AT
Date of test |  |  |  | 2025-10-29 |  |  | 2025-11-04
Sample details
In accordance with (Customer's instructions / IEC / IS / ANSI)
Serial Number
Condition of the sample (New / Re-conditioned / After test / Good)
Atmospheric conditions |  |  |  | BT |  |  | AT
Amb °C |  |  |  | 26.8 |  |  | 26.7
RH - % |  |  |  | 79.8 |  |  | 71
Type
Description of test |  |  |  |  | BT |  | AT
Vector Group |  | Vector Group |  |  | Dyn11
I/R test (GΩ) |  | H.V. to Earth |  |  | 4.19 |  | 6.11
|  | L.V. to Earth |  |  | 1.22 |  | 1.35
|  | H.V. to L.V. |  |  | 6.56 |  | 7.81
Induced over voltage test |  | Voltage - V |  |  | 866
|  | Current - A |  |  | 1.58 |  | 1.66
|  | Frequency - Hz |  |  | 100
|  | Duration - Seconds |  |  | 60
|  | Observation |  |  | No disruptive discharge, withstood
High voltage power frequency test |  | H.V. test voltage - kV |  |  | 28
|  | H.V. duration - seconds |  |  | 60
H.V. current - mA
|  | H.V. observation |  |  | No disruptive discharge, withstood
|  | L.V. test voltage - kV |  |  | 3
|  | L.V. duration - seconds |  |  | 60
L.V. current - mA
|  | L.V. observation |  |  | No disruptive discharge, withstood
Voltage ratio
Tap number | BT |  |  | AT
| A(U) | B(V) | C(W) | A(U) | B(V) | C(W)
1 | 46.38 | 46.36 | 46.26 | 46.37 | 46.37 | 46.26
2 | 45.22 | 45.22 | 45.12 | 45.23 | 45.23 | 45.13
3 | 44.1 | 44.09 | 44.06 | 44.11 | 44.09 | 44.07
4 | 43.02 | 43.01 | 42.96 | 43.03 | 43.05 | 43
5 | 41.92 | 41.92 | 41.92 | 41.93 | 41.92 | 41.92
6 | 40.82 | 40.86 | 40.86 | 40.81 | 40.86 | 40.81
7 | 39.73 | 39.72 | 39.72 | 39.73 | 39.72 | 39.72
Customer's Signature |  |  |  | Tested by |  |  | Test Engineer
Instruments / Equipment used | Serial Number
I/R test kit
DTM / RH Indicator
Turns ratio meter
H.V. Test kit
DVDF Test kit
Time interval meter
DMM (1)
DMM (2)
APPROVED BY: Document: FORMS & FORMATS SECTION : 45 PAGE NO.: 1 of 1 ISSUE NO.: 2 REVISION No.: 00 DATE : 01-08-2014