## Proforma for transformers
Proforma for transformers
CPRI Short Circuit Laboratory - form: Aletheia template proforma (version 1). Fill the yellow cells only; do not move or rename them.
Rating (kVA) | 250 | HV voltage (V) | 11000
LV voltage (V) | 433 | Highest system voltage (kV) | 12
Insulation levels | HV LI 75 kV / AC 28 kV rms; LV AC 3 kV rms | Impedance at 75 C (%) | 4.5
Phases | 3 | Frequency (Hz) | 50
Vector group | Dyn11 | Cooling | ONAN
Tapping range | +5% to -10% in steps of 2.5% (7 taps) | Guaranteed total loss, 50% load (W) | 980
Guaranteed total loss, 100% load (W) | 2930 | Oil quantity (l) | 460
Month / year of manufacture | 10/2025 | Construction | Oil immersed, non-sealed, outdoor; LV helical/spiral copper, HV crossover copper; circular coils; CRGO core; tank plain/corrugated
Top-oil rise limit (K) | 35 | Winding rise limit (K) | 40
Energy efficiency level |  | Coil
Core material |  | LV winding details
HV winding details
Tests to be carried out
Test
Dynamic ability to withstand short circuit (with thermal short)
Temperature rise test
Pressure test (IS 2026)
Vacuum test (IS 1180)
No load current at 112.5%
Oil leakage test