## Losses logsheet (no-load)
Losses logsheet (no-load)
CPRI Short Circuit Laboratory - form: Aletheia template noload (version 1). Fill the yellow cells only; do not move or rename them.
Test series no. (as written) | 25T1656 |  | Sample code no. (as written) | HVD25S0847
Rated voltage, 100% (V) | 433.06 |  | Voltage at 112.5% (V) | 487.32
Remarks | Within limit at 100% and 112.5%
No-load readings
Condition | Voltage (V) |  |  | Average V | Current (A) |  |  | Average I | Watts |  |  | Total W | Frequency (Hz) | Corrected loss (W)
| V1 | V2 | V3 |  | I1 | I2 | I3 |  | W1 | W2 | W3
BT | 251.133 | 252.814 | 246.166 | 250.03 | 1.907 | 1.445 | 1.714 | 1.689 | 109.18 | 84.52 | 189.22 | 382.92 | 49.95 | 383.18
AT | 250.458 | 252.724 | 246.849 | 250.01 | 1.893 | 1.438 | 1.73 | 1.687 | 104.53 | 88.28 | 190.49 | 383.3 | 49.99 | 383.26
112.5% | 266.596 | 284.378 | 293.094 | 281.356 | 4.681 | 3.937 | 4.165 | 4.261 | 98.86 | 165.57 | 288.72 | 553.73 | 49.94 | 548.36