## Short-circuit logsheet
Short-circuit logsheet
CPRI Short Circuit Laboratory - form: Aletheia template sc (version 1). Fill the yellow cells only; do not move or rename them.
Test series no. (as written) | CPRIBLRSCL25T1654 |  | Sample code no. (as written) | HVD25S0847
Date of test | 31-10-2025 |  | Condition of sample | As after routine test
Observation during test | No abnormalities |  | Observation after test | No abnormalities
Untanking / inspection | Conductor, core & clampings: no visible damage; spacers/support blocks: intact; oil: clear
Required test currents
Tap | Required rms (kA) | Required peak (kA)
NT | 7.61 | 16.73
HT | 7.5 | 16.61
LT | 7.43 | 16.2
Oscillograms
Oscillogram no. | Tap position | Setting (as logged) | Peak (kA) | RMS U (kA) | RMS V (kA) | RMS W (kA) | Average rms (kA) | Duration (s) | Note
S001 | NT | 145 | 5.32 | 2.07 | 2.11 | 2.07 | 2.08 | 0.54 | calibration
S002 | NT | 145 | 16.8 | 7.45 | 7.59 | 7.53 | 7.53 | 0.54
S003 | NT | 155 | 16.82 | 7.57 | 7.76 | 7.65 | 7.66 | 0.54
S004 | NT | 155 | 16.74 | 7.61 | 7.85 | 7.68 | 7.71 | 0.54
S005 | HT | 180 | 16.89 | 7.48 | 7.45 | 7.62 | 7.52 | 0.54
S006 | HT | 180 | 16.78 | 7.53 | 7.46 | 7.64 | 7.54 | 0.54
S007 | HT | 180 | 16.73 | 7.51 | 7.44 | 7.65 | 7.53 | 0.54
S008 | LT | 40 | 16.49 | 7.68 | 7.56 | 7.64 | 7.63 | 0.54
S009 | LT | 40 | 16.34 | 7.47 | 7.4 | 7.44 | 7.44 | 0.54
S010 | LT | 40 | 16.26 | 7.5 | 7.39 | 7.47 | 7.45 | 0.54
S011 | NT | 70 |  | 7.53 | 7.58 | 7.55 | 7.55 | 2.01 | thermal