## Temperature-rise logsheet
Temperature-rise logsheet
CPRI Short Circuit Laboratory - form: Aletheia template temp (version 1). Fill the yellow cells only; do not move or rename them.
Test series no. (as written) | 25T1654 |  | Sample code no. (as written) | HVD25S0847
Date(s) of test | 09-11-2025 to 10-11-2025 |  | Tap position | LT
Test current (A) | 14.58 |  | No-load loss (W) | 383.26
Full-load loss (W) | 2239.94 |  | Total loss injected (W) | 2623.2
HV cold resistance (ohm) | 3.554 |  | LV cold resistance (mohm) | 3.8844
Ambient at cold resistance (C) | 25.9 |  | HV hot resistance (ohm) | 4.0464
LV hot resistance (mohm) | 4.3425 |  | Ambient at shut-down (C) | 22.85
Correction used in formula (K) | 0.475 |  | Correction written on sheet (K) | 0.275
Top-oil rise, as logged (K) | 26.01 |  | HV winding rise, as logged (K)
LV winding rise, as logged (K) |  |  | Winding material constant (235 Cu / 225 Al) | 235
Hourly readings
Hour | Top oil (C) | Bottom oil (C) | Ambient 1 (C) | Ambient 2 (C) | Ambient 3 (C)
0 | 23.1 | 21.65 | 21.1 | 21 | 21.3
1 | 29.8 | 23.25 | 20.8 | 20.65 | 21.15
2 | 34.55 | 26 | 20.65 | 20.45 | 21.05
3 | 38.8 | 28.55 | 20.45 | 20.95 | 20.85
4 | 41.55 | 30.5 | 20.35 | 20.05 | 20.75
5 | 43.45 | 31.8 | 20.35 | 20 | 20.75
6 | 44 | 32.2 | 20.2 | 19.8 | 20.6
7 | 45.5 | 33 | 20.1 | 19.6 | 20.5
8 | 46 | 33.6 | 20 | 19.5 | 20.4
9 | 46.55 | 34.05 | 19.8 | 19.35 | 20.3
10 | 46.9 | 35.5 | 20.1 | 19.75 | 20.45
11 | 47.95 | 36.65 | 21.1 | 20.8 | 21.1
12 | 49 | 37.9 | 22.85 | 22.85 | 22.85