## Pressure oil-leakage logsheet
Pressure / oil-leakage logsheet
CPRI Short Circuit Laboratory - form: Aletheia template pressure (version 1). Fill the yellow cells only; do not move or rename them.
Test series no. (as written) | 25T1654 | Sample code no. (as written) | HVD25S0847
Ambient (C) | 25 | Atmospheric pressure (kPa)
Plate / tank height (m) | 1.6 | Routine pressure (kPa) | 35
Routine pressure duration (min) | 10 | Routine pressure date | 14-11-2025
Routine pressure observation | No leakage at any point | Type tests date(s) | 14-11-2025 / 17-11-2025
Type pressure (kPa) | 80 | Type pressure duration (min) | 30
Pressure: max deflection, as logged (mm) | 1.08 | Pressure test observation | Within limits
Vacuum (mmHg) | 500 | Vacuum duration (min) | 30
Vacuum: max deflection, as logged (mm) | 2.87 | Vacuum test observation | Within limits
Oil leakage pressure (kPa) | 28 | Oil head (kPa) | 14
Oil leakage duration (h) | 8 | Oil leakage date | 13-11-2025
Oil leakage observation | No leakage at any point
Pressure test: deflection points (mm)
Pressure: before | Pressure: after
259.99 | 259.64
174.3 | 174.44
181.35 | 181.13
276.99 | 275.91
Vacuum test: deflection points (mm)
Vacuum: before | Vacuum: after
259.4 | 261.26
174.19 | 174.93
186.01 | 186.28
231.09 | 233.96