## request
field | value
customer | A.P. Transformers
address | SP24 & 95H/1 (SP), Ambattur Indl Estate, Chennai - 600058
sample | 3 Phase Distribution Transformer
rating | 250 kVA / 11 kV / 433 V, 3PH, 50 Hz, copper wound, non-sealed, outdoor, tapping +5% to -10% (7 taps)
type | ONAN outdoor type distribution transformer
serial | "1098"
drawings | APT/250-11/001, APT/250-11/001B
criteria | As per standard (IS 1180)
samples | 1
tests | Type test
witness | Mr. Vivekanand Krishna (customer representative)
dispatch | Handed over to person
conformity | Yes - (i) compliance per standard; MU reported if required
take_back | Yes
condition | Suitable for testing

## proforma
field | value
kva | 250
hv | 11000
lv | 433
hv_max_kv | 12
bil | HV LI 75 kV / AC 28 kV rms; LV AC 3 kV rms
z_pct | 4.5
phases | 3
freq | 50
vector | Dyn11
cooling | ONAN
taps | +5% to -10% in steps of 2.5% (7 taps)
loss50 | 980
loss100 | 2930
oil_l | "460"
mfg | 10/2025
construction | Oil immersed, non-sealed, outdoor; LV helical/spiral copper, HV crossover copper; circular coils; CRGO core; tank plain/corrugated
limits.oil | 35
limits.wdg | 40
tests[0] | Dynamic ability to withstand short circuit (with thermal short)
tests[1] | Temperature rise test
tests[2] | Pressure test (IS 2026)
tests[3] | Vacuum test (IS 1180)
tests[4] | No load current at 112.5%
tests[5] | Oil leakage test

## work
field | value
series | CPRIBLRSCL25T1654
sample | HVD25S0847
customer | M/s. A.P. Transformers, Chennai
start | 28-10-2025
completed | 18-11-2025
standard | IS 1180 (latest: yes)
allotted | Sh. NMR / Sh. NK / Mr. Utley
engineer | P. Naveenkumar

## losses
field | value
nll_bt | 383.18
nll_at | 383.26
cols[0] | tap
cols[1] | z
cols[2] | x
cols[3] | xchg
cols[4] | rhv
cols[5] | rlv
cols[6] | ll100
cols[7] | xr
cols[8] | ipk
cols[9] | irms
cols[10] | stray
cols[11] | ll50
cols[12] | t50
cols[13] | t100
rows[0][0] | NTBT
rows[0][1] | 4.38
rows[0][2] | 4.299
rows[0][3] | null
rows[0][4] | 7.101
rows[0][5] | 2.317
rows[0][6] | 2102.74
rows[0][7] | 5.112
rows[0][8] | 16.73
rows[0][9] | 7.61
rows[0][10] | 107.62
rows[0][11] | 524.91
rows[0][12] | 908.09
rows[0][13] | 2485.92
rows[1][0] | NTAT
rows[1][1] | 4.387
rows[1][2] | 4.306
rows[1][3] | -0.163
rows[1][4] | 7.098
rows[1][5] | 2.318
rows[1][6] | 2101.21
rows[1][7] | null
rows[1][8] | null
rows[1][9] | null
rows[1][10] | 106.21
rows[1][11] | 523.61
rows[1][12] | 906.87
rows[1][13] | 2484.47
rows[2][0] | HTBT
rows[2][1] | 4.442
rows[2][2] | 4.365
rows[2][3] | null
rows[2][4] | 7.504
rows[2][5] | 2.317
rows[2][6] | 2056.03
rows[2][7] | 5.31
rows[2][8] | 16.61
rows[2][9] | 7.5
rows[2][10] | 111.77
rows[2][11] | null
rows[2][12] | null
rows[2][13] | 2439.21
rows[3][0] | HTAT
rows[3][1] | 4.446
rows[3][2] | 4.369
rows[3][3] | -0.092
rows[3][4] | 7.502
rows[3][5] | 2.318
rows[3][6] | 2054.67
rows[3][7] | null
rows[3][8] | null
rows[3][9] | null
rows[3][10] | 110.09
rows[3][11] | null
rows[3][12] | null
rows[3][13] | 2437.93
rows[4][0] | LTBT
rows[4][1] | 4.487
rows[4][2] | 4.397
rows[4][3] | null
rows[4][4] | 6.346
rows[4][5] | 2.317
rows[4][6] | 2240.03
rows[4][7] | 4.907
rows[4][8] | 16.2
rows[4][9] | 7.43
rows[4][10] | 118.6
rows[4][11] | null
rows[4][12] | null
rows[4][13] | 2623.21
rows[5][0] | LTAT
rows[5][1] | 4.496
rows[5][2] | 4.406
rows[5][3] | -0.205
rows[5][4] | 6.343
rows[5][5] | 2.318
rows[5][6] | 2239.94
rows[5][7] | null
rows[5][8] | null
rows[5][9] | null
rows[5][10] | 118.58
rows[5][11] | null
rows[5][12] | null
rows[5][13] | 2623.2

## resistance
field | value
date_bt | 29-10-2025
date_at | 04-11-2025
oil_top[0] | 25.5
oil_top[1] | 27
oil_bot[0] | 23.9
oil_bot[1] | 24.8
hv.N[0][0] | 3.9736
hv.N[0][1] | 3.9558
hv.N[0][2] | 3.969
hv.N[1][0] | 3.989
hv.N[1][1] | 3.9734
hv.N[1][2] | 3.9864
hv.H[0][0] | 4.2028
hv.H[0][1] | 4.1822
hv.H[0][2] | 4.1874
hv.H[1][0] | 4.22
hv.H[1][1] | 4.1988
hv.H[1][2] | 4.2092
hv.L[0][0] | 3.5476
hv.L[0][1] | 3.5398
hv.L[0][2] | 3.5458
hv.L[1][0] | 3.5612
hv.L[1][1] | 3.554
hv.L[1][2] | 3.5622
lv[0][0] | 3.8716
lv[0][1] | 3.865
lv[0][2] | 3.9074
lv[1][0] | 3.897
lv[1][1] | 3.8844
lv[1][2] | 3.9248

## noload
field | value
v100 | 433.06
v1125 | 487.32
rows[0][0] | BT
rows[0][1][0] | 251.133
rows[0][1][1] | 252.814
rows[0][1][2] | 246.166
rows[0][2] | 250.03
rows[0][3][0] | 1.907
rows[0][3][1] | 1.445
rows[0][3][2] | 1.714
rows[0][4] | 1.689
rows[0][5][0] | 109.18
rows[0][5][1] | 84.52
rows[0][5][2] | 189.22
rows[0][6] | 382.92
rows[0][7] | 49.95
rows[0][8] | 383.18
rows[1][0] | AT
rows[1][1][0] | 250.458
rows[1][1][1] | 252.724
rows[1][1][2] | 246.849
rows[1][2] | 250.01
rows[1][3][0] | 1.893
rows[1][3][1] | 1.438
rows[1][3][2] | 1.73
rows[1][4] | 1.687
rows[1][5][0] | 104.53
rows[1][5][1] | 88.28
rows[1][5][2] | 190.49
rows[1][6] | 383.3
rows[1][7] | 49.99
rows[1][8] | 383.26
rows[2][0] | 112.5%
rows[2][1][0] | 266.596
rows[2][1][1] | 284.378
rows[2][1][2] | 293.094
rows[2][2] | 281.356
rows[2][3][0] | 4.681
rows[2][3][1] | 3.937
rows[2][3][2] | 4.165
rows[2][4] | 4.261
rows[2][5][0] | 98.86
rows[2][5][1] | 165.57
rows[2][5][2] | 288.72
rows[2][6] | 553.73
rows[2][7] | 49.94
rows[2][8] | 548.36
remarks | Within limit at 100% and 112.5%

## routine
field | value
date_bt | 29-10-2025
date_at | 04-11-2025
amb[0] | 26.8
amb[1] | 26.7
rh[0] | 79.8
rh[1] | 71
vector | Dyn11
ir.HV-Earth[0] | 4.19
ir.HV-Earth[1] | 6.11
ir.LV-Earth[0] | 1.22
ir.LV-Earth[1] | 1.35
ir.HV-LV[0] | 6.56
ir.HV-LV[1] | 7.81
induced.v | 866
induced.f | 100
induced.t | 60
induced.i[0] | 1.58
induced.i[1] | 1.66
induced.obs | No disruptive discharge, withstood
hvac.kv | 28
hvac.t | 60
hvac.obs | No disruptive discharge, withstood
lvac.kv | 3
lvac.t | 60
lvac.obs | No disruptive discharge, withstood
ratio.BT[0][0] | 46.38
ratio.BT[0][1] | 46.36
ratio.BT[0][2] | 46.26
ratio.BT[1][0] | 45.22
ratio.BT[1][1] | 45.22
ratio.BT[1][2] | 45.12
ratio.BT[2][0] | 44.1
ratio.BT[2][1] | 44.09
ratio.BT[2][2] | 44.06
ratio.BT[3][0] | 43.02
ratio.BT[3][1] | 43.01
ratio.BT[3][2] | 42.96
ratio.BT[4][0] | 41.92
ratio.BT[4][1] | 41.92
ratio.BT[4][2] | 41.92
ratio.BT[5][0] | 40.82
ratio.BT[5][1] | 40.86
ratio.BT[5][2] | 40.86
ratio.BT[6][0] | 39.73
ratio.BT[6][1] | 39.72
ratio.BT[6][2] | 39.72
ratio.AT[0][0] | 46.37
ratio.AT[0][1] | 46.37
ratio.AT[0][2] | 46.26
ratio.AT[1][0] | 45.23
ratio.AT[1][1] | 45.23
ratio.AT[1][2] | 45.13
ratio.AT[2][0] | 44.11
ratio.AT[2][1] | 44.09
ratio.AT[2][2] | 44.07
ratio.AT[3][0] | 43.03
ratio.AT[3][1] | 43.05
ratio.AT[3][2] | 43
ratio.AT[4][0] | 41.93
ratio.AT[4][1] | 41.92
ratio.AT[4][2] | 41.92
ratio.AT[5][0] | 40.81
ratio.AT[5][1] | 40.86
ratio.AT[5][2] | 40.81
ratio.AT[6][0] | 39.73
ratio.AT[6][1] | 39.72
ratio.AT[6][2] | 39.72

## sc
field | value
date | 31-10-2025
condition | As after routine test
required.NT[0] | 7.61
required.NT[1] | 16.73
required.HT[0] | 7.5
required.HT[1] | 16.61
required.LT[0] | 7.43
required.LT[1] | 16.2
shots[0][0] | S001
shots[0][1] | NT
shots[0][2] | 145
shots[0][3] | 5.32
shots[0][4] | 2.07
shots[0][5] | 2.11
shots[0][6] | 2.07
shots[0][7] | 2.08
shots[0][8] | 0.54
shots[0][9] | calibration
shots[1][0] | S002
shots[1][1] | NT
shots[1][2] | 145
shots[1][3] | 16.8
shots[1][4] | 7.45
shots[1][5] | 7.59
shots[1][6] | 7.53
shots[1][7] | 7.53
shots[1][8] | 0.54
shots[1][9] | ""
shots[2][0] | S003
shots[2][1] | NT
shots[2][2] | 155
shots[2][3] | 16.82
shots[2][4] | 7.57
shots[2][5] | 7.76
shots[2][6] | 7.65
shots[2][7] | 7.66
shots[2][8] | 0.54
shots[2][9] | ""
shots[3][0] | S004
shots[3][1] | NT
shots[3][2] | 155
shots[3][3] | 16.74
shots[3][4] | 7.61
shots[3][5] | 7.85
shots[3][6] | 7.68
shots[3][7] | 7.71
shots[3][8] | 0.54
shots[3][9] | ""
shots[4][0] | S005
shots[4][1] | HT
shots[4][2] | 180
shots[4][3] | 16.89
shots[4][4] | 7.48
shots[4][5] | 7.45
shots[4][6] | 7.62
shots[4][7] | 7.52
shots[4][8] | 0.54
shots[4][9] | ""
shots[5][0] | S006
shots[5][1] | HT
shots[5][2] | 180
shots[5][3] | 16.78
shots[5][4] | 7.53
shots[5][5] | 7.46
shots[5][6] | 7.64
shots[5][7] | 7.54
shots[5][8] | 0.54
shots[5][9] | ""
shots[6][0] | S007
shots[6][1] | HT
shots[6][2] | 180
shots[6][3] | 16.73
shots[6][4] | 7.51
shots[6][5] | 7.44
shots[6][6] | 7.65
shots[6][7] | 7.53
shots[6][8] | 0.54
shots[6][9] | ""
shots[7][0] | S008
shots[7][1] | LT
shots[7][2] | 40
shots[7][3] | 16.49
shots[7][4] | 7.68
shots[7][5] | 7.56
shots[7][6] | 7.64
shots[7][7] | 7.63
shots[7][8] | 0.54
shots[7][9] | ""
shots[8][0] | S009
shots[8][1] | LT
shots[8][2] | 40
shots[8][3] | 16.34
shots[8][4] | 7.47
shots[8][5] | 7.4
shots[8][6] | 7.44
shots[8][7] | 7.44
shots[8][8] | 0.54
shots[8][9] | ""
shots[9][0] | S010
shots[9][1] | LT
shots[9][2] | 40
shots[9][3] | 16.26
shots[9][4] | 7.5
shots[9][5] | 7.39
shots[9][6] | 7.47
shots[9][7] | 7.45
shots[9][8] | 0.54
shots[9][9] | ""
shots[10][0] | S011
shots[10][1] | NT
shots[10][2] | 70
shots[10][3] | null
shots[10][4] | 7.53
shots[10][5] | 7.58
shots[10][6] | 7.55
shots[10][7] | 7.55
shots[10][8] | 2.01
shots[10][9] | thermal
during | No abnormalities
after | No abnormalities
inspection | Conductor, core & clampings: no visible damage; spacers/support blocks: intact; oil: clear

## temp
field | value
dates | 09-11-2025 to 10-11-2025
nll | 383.26
fll | 2239.94
total | 2623.2
tap | LT
current | 14.58
rhv_cold | 3.554
rlv_cold | 3.8844
amb_cold | 25.9
hours[0][0] | 0
hours[0][1] | 23.1
hours[0][2] | 21.65
hours[0][3] | 21.1
hours[0][4] | 21
hours[0][5] | 21.3
hours[1][0] | 1
hours[1][1] | 29.8
hours[1][2] | 23.25
hours[1][3] | 20.8
hours[1][4] | 20.65
hours[1][5] | 21.15
hours[2][0] | 2
hours[2][1] | 34.55
hours[2][2] | 26
hours[2][3] | 20.65
hours[2][4] | 20.45
hours[2][5] | 21.05
hours[3][0] | 3
hours[3][1] | 38.8
hours[3][2] | 28.55
hours[3][3] | 20.45
hours[3][4] | 20.95
hours[3][5] | 20.85
hours[4][0] | 4
hours[4][1] | 41.55
hours[4][2] | 30.5
hours[4][3] | 20.35
hours[4][4] | 20.05
hours[4][5] | 20.75
hours[5][0] | 5
hours[5][1] | 43.45
hours[5][2] | 31.8
hours[5][3] | 20.35
hours[5][4] | 20
hours[5][5] | 20.75
hours[6][0] | 6
hours[6][1] | 44
hours[6][2] | 32.2
hours[6][3] | 20.2
hours[6][4] | 19.8
hours[6][5] | 20.6
hours[7][0] | 7
hours[7][1] | 45.5
hours[7][2] | 33
hours[7][3] | 20.1
hours[7][4] | 19.6
hours[7][5] | 20.5
hours[8][0] | 8
hours[8][1] | 46
hours[8][2] | 33.6
hours[8][3] | 20
hours[8][4] | 19.5
hours[8][5] | 20.4
hours[9][0] | 9
hours[9][1] | 46.55
hours[9][2] | 34.05
hours[9][3] | 19.8
hours[9][4] | 19.35
hours[9][5] | 20.3
hours[10][0] | 10
hours[10][1] | 46.9
hours[10][2] | 35.5
hours[10][3] | 20.1
hours[10][4] | 19.75
hours[10][5] | 20.45
hours[11][0] | 11
hours[11][1] | 47.95
hours[11][2] | 36.65
hours[11][3] | 21.1
hours[11][4] | 20.8
hours[11][5] | 21.1
hours[12][0] | 12
hours[12][1] | 49
hours[12][2] | 37.9
hours[12][3] | 22.85
hours[12][4] | 22.85
hours[12][5] | 22.85
rhv_hot | 4.0464
rlv_hot | 4.3425
amb_sd | 22.85
corr | 0.475
corr_written | 0.275
oil_rise_reported | 26.01
material_k | 235

## pressure
field | value
amb | 25
plate_m | 1.6
routine.kpa | 35
routine.min | 10
routine.date | 14-11-2025
routine.obs | No leakage at any point
type.date | 14-11-2025 / 17-11-2025
type.pressure.kpa | 80
type.pressure.min | 30
type.pressure.max | 1.08
type.pressure.obs | Within limits
type.pressure.pts[0][0] | 259.99
type.pressure.pts[0][1] | 259.64
type.pressure.pts[1][0] | 174.3
type.pressure.pts[1][1] | 174.44
type.pressure.pts[2][0] | 181.35
type.pressure.pts[2][1] | 181.13
type.pressure.pts[3][0] | 276.99
type.pressure.pts[3][1] | 275.91
type.vacuum.mmhg | 500
type.vacuum.min | 30
type.vacuum.max | 2.87
type.vacuum.obs | Within limits
type.vacuum.pts[0][0] | 259.4
type.vacuum.pts[0][1] | 261.26
type.vacuum.pts[1][0] | 174.19
type.vacuum.pts[1][1] | 174.93
type.vacuum.pts[2][0] | 186.01
type.vacuum.pts[2][1] | 186.28
type.vacuum.pts[3][0] | 231.09
type.vacuum.pts[3][1] | 233.96
leak.kpa | 28
leak.head_kpa | 14
leak.hrs | 8
leak.date | 13-11-2025
leak.obs | No leakage at any point

## ids
field | value
work[0] | CPRIBLRSCL25T165H
work[1] | HVD25S08H7
losses[0] | CPRIBLRSCL25T1654
losses[1] | HVD25S0847
resistance[0] | 25T1656
resistance[1] | HVD25S0847
noload[0] | 25T1656
noload[1] | HVD25S0847
routine[0] | 25T1654
routine[1] | HVD25S0867
sc[0] | CPRIBLRSCL25T1654
sc[1] | HVD25S0847
temp[0] | 25T1654
temp[1] | HVD25S0847
pressure[0] | 25T1654
pressure[1] | HVD25S0847